## Instructions
What Is the Asset Management Process?
Asset management consists of the following five steps:
1. Taking an inventory. Before you can manage your assets, you need to know what assets you have and what condition they are in. This information will help you schedule rehabilitations and replacements of your assets.
2. Prioritizing your assets. Your water system probably has a limited budget. Prioritizing your assets will ensure that you allocate funds to the rehabilitation or replacement of your most important assets.
3. Developing an asset management plan. Planning for the rehabilitation and replacement of your assets includes estimating how much money you will need each year to maintain the operation of your system each year. This includes developing a budget and calculating your required reserves.
4. Implementing your asset management plan. Once you have determined how much money you will have to set aside each year and how much additional funding (if any) you will need to match that amount, you need to work with your management and customers and with regulators to carry out your plan and ensure that you have the technical and financial means to deliver safe water to your customers.
5. Reviewing and revising your asset management plan. Once you have developed an asset management plan, do not stick it in a drawer and forget about it! Your asset management plan should be used to help you shape your operations. It is a flexible document that should evolve as you gain more information and as priorities shift.
Instructions: Instructions on completing the worksheet can be found in Asset Management: A Handbook for Small Wate Systemshere - https://nepis.epa.gov/Exe/ZyPDF.cgi?Dockey=P100U7T2.txt

## Inventory Worksheet
System Inventory Worksheet | [6 empty] | Instructions
Date worksheet completed/updated: 1 | [6 empty] | Step #1 | Enter the date. Circle whether you are completing or updating the worksheet and fill in the date. You should update this worksheet at least once a year. You can either make minor adjustments to the worksheet as the condition of your assets change, or start a new worksheet each year.
2 Asset | 3 Expected Useful Life | 4 Condition | 5 Service History | 6 Adjusted Useful Life | 7 Age | 8 Remaining Useful Life | Step #2 | Identify your assets. Write in each of your system’s assets. Be as specific as possible by providing location, manufacturer, or some other identifier for each asset. List separately assets made of different materials or installed at different times. For example, you might list a section of your distribution system as “10-inch PVC on Main St.” You can make a copy of this worksheet if you need more room to list assets.
[7 empty] | Step #3 | Fill in expected useful life. Use the manufacturer’s recommendation or the list provided in the box on page 9 to enter the expected useful life for each asset.
[7 empty] | Step #4 | Describe assets’ condition. Briefly describe the condition of each asset. Focus especially on conditions that may influence the useful life (for example, rust or broken parts).
[7 empty] | Step #5 | Describe service history. Briefly describe the service history of each asset. Include routine maintenance activities as well as any repairs and rehabilitations. List how often you have made repairs and rehabilitations.
[7 empty] | Step #6 | Estimate the adjusted useful life for each asset. Using the Expected Useful Life (step 3) as a guide, estimate the adjusted useful life for each of your assets by considering its current condition (step 4) and itsservice history (step 5). - If your asset is in poor condition, has not been properly maintained, or faces other challenges (poor water or soil quality, excessive use, etc.), then the adjusted useful life is likely to be less than the lower end of theexpected useful life range. - If your asset is in good condition, has been properlymaintained, and faces average water quality, then you can use the average useful life value. However, you may want to use the lower end of the range to be more conservative and help ensure that you are prepared to replace the asset. - If your asset is in good condition, has been properly maintained, and faces average water quality, then you can use the average useful life value. However, you may want to use the lower end of the range to be more conservative and help ensure that you are prepared to replace the asset.
[7 empty] | Step #7 | Record age. For each asset, fill in how long the asset has been in use. If the asset has been previously used by another system, you should list the total age, not just the length of time your system has used it.
[7 empty] | Step #8 | Calculate the remaining useful life. For each asset, calculate the remaining useful life by subtracting its age (step 7) from its adjusted useful life (step 6)
Example System Inventory Worksheet
Date Worksheet Completed/Updated: 8/14/02
Asset | Expected Useful Life | Condition | Service History | Adjusted Useful Life | Age | Remaining Useful Life
Well 1 (1993) | 30 | Good |  | 30 | 9 | 21
Well 1 pump | 10 | Good | Rehab (1996) | 10 | 9 | 1
Well 2 (1993) | 30 | Good |  | 30 | 9 | 21
Well 2 pump | 10 | Good | Rehab (1998) | 10 | 9 | 1
Pumphouse (1993) | 30 | Good |  | 30 | 9 | 21
Electrical components | 10 | Some corrosion | Rehab (1994) | 10 | 9 | 1
Chlorinator (1993) | 10 | Good | Rehab (1998) | 5 | 3 | 2
Storage tank 1 (1993) | 40 | Good | Rehab (2000) - $17,000 | 40 | 9 | 31
Storage tank 2 (1993) | 40 | Good | Rehab (2000) - $17,000 | 40 | 9 | 31
Storage tank 3 (2000) | 40 | Almost new |  | 40 | 2 | 38
Distribution System:
Hydrants (15) | 40 | Unknown |  | 40 | 9 | 11
Valves (45) | 40 | Unknown | 6 valves don’t work | 40 | 9 | 11
6-inch (PVC) | 60 | Unknown |  | 60 | 9 | 51
4-inch (PVC) | 60 | Unknown |  | 60 | 9 | 51
2-inch (PVC) | 60 | Unknown | Repair breaks (2/year) | 60 | 9 | 51

## Prioritization Worksheet
Prioritization Worksheet |  |  |  |  | Instructions
Date worksheet completed/updated: 1 |  |  |  |  | Step #1 | Enter the date. Circle whether you are completing or updating the worksheet and fill in the date. You should update this worksheet at least every year. You can either make minor adjustments to the worksheet as your priorities change or problems are addressed, or start a new worksheet each year.
2 Asset | 3 Expected Useful Life | 4 Importance | 5 Redundancy | 6 Priority (1 is high)
[5 empty] | Step #2 | List your assets. Copy your list of assets from step 2 of the System Inventory Worksheet.
[5 empty] | Step #3 | Enter assets’ remaining useful life. For each of your assets, copy the remaining useful life from step 8 of the System Inventory Worksheet.
[5 empty] | Step #4 | Describe assets’ importance. Briefly describe the importance of each of the assets to the operation of your system and the protection of public health. Assets that are required in order to keep the system running are usually more important than those that just make operation more efficient.
[5 empty] | Step #5 | Describe assets’ redundancy. Briefly describe the redundancy of each of the assets. Are there assets that can do the same job, even if they cannot do it as well?
[5 empty] | Step #6 | Evaluate assets’ priority. - Considering remaining useful life, importance, redundancy, and any other important factors, rank your assets in terms of how important it is to reserve money for them. Write “1” next to the asset with the highest priority, “2” next to the asset with the next highest priority, and so on. You may find that you have more than one asset with the same level of priority. You can assign the same ranking to all assets with the same priority. - Assets with a shorter remaining useful life should have a higher priority (lower number) because you will need to rehabilitate or replace them relatively soon. - Assets that are more important to your ability to deliver safe water should have a high priority (lower number), because of public health protection goals. - Assets for which there is less redundancy should have a high priority (lower number), because your system will have trouble continuing to operate without them.
EXAMPLE Prioritization Worksheet
Date Worksheet Completed/Updated: | 2002-08-14
Asset | Remaining Useful Life | Importance | Redundancy | Priority (1 is high)
Well 1 (1993) | 21 | Needed for service | Other well, but need backup | 6
Well 1 pump | 1 | Needed for service | Other well, but need backup | 3
Well 2 (1993) | 21 | Needed for service | Other well, but need backup | 6
Well 2 pump | 1 | Needed for service | Other well, but need backup | 3
Pumphouse (1993) | 21 | Needed for service | Other well, but need backup | 6
Electrical components | 1 | Needed for control | No redundancy - corrosion | 2
Chlorinator (1993) | 2 | Mandatory | No redundancy - need backup | 1
Storage tank 1 (1993) | 31 | Need for fire flow and demand | Other tanks | 6
Storage tank 2 (1993) | 31 | Need for fire flow and demand | Other tanks | 6
Storage tank 3 (2000) | 38 | Need for fire flow and demand | Other tanks | 6
Distribution System:
Hydrants (15) | 11 | Needed for public safety | Other hydrants | 5
Valves (45) | 11 | Needed for isolation | Other valves, but some are out of service | 4
6-inch (PVC) | 51 | Needed for delivery | No redundancy | 6
4-inch (PVC) | 51 | Needed for delivery | No redundancy | 6
2-inch (PVC) | 51 | Needed for delivery | No redundancy | 6

## Required Reserve
Required Reserve Worksheet |  |  |  |  | Instructions
Date worksheet completed/updated: 1
Asset (list from highest to lowest priority) 2 | Activity 3 | Years until action needed 4 | Cost ($) 5 | Reserve Required Current Year 6 | Step #1 | Enter the date. Circle whether you are completing or updating the worksheet and fill in the date. You should update this worksheet at least once a year. You can either make minor adjustments to the worksheet, or start a new worksheet each year.
[5 empty] | Step #2 | List your prioritized assets. List the assets from the Prioritization Worksheet. List the assets in order, with the highest priority assets (lowest number) first.
[5 empty] | Step #3 | List activities. For each asset, list the rehabilitation and replacement activities that you expect to perform over the next five years. Provide enough detail for each activity so that you can determine the cost of the activity.
[5 empty] | Step #4 | Estimate years until action needed. For each activity, fill in the number of years before you will need to do that task. For annual activities, enter “1.” For replacement activities, enter the remaining useful life you estimated in step 8 of the System Inventory Worksheet.
[5 empty] | Step #5 | Estimate cost. Fill in the expected cost for each activity. Make sure to include the complete cost, including preparation, clean- up, removal, and disposal of any waste. If you expect to sell an asset at the end of its useful life, subtract the estimated sale price from the cost of a new item and enter the difference.
[5 empty] | Step #6 | Calculate the reserve required per year. For each asset, calculate the reserve required by dividing the cost by the years until the action is needed. This is the estimated amount of money that your system needs to set aside per year for that asset.
7 Total Reserve in the current year
Note: The required reserve worksheet only helps you account for the additional funds you required to rehabilitate or replace your assets. Standard O&M costs are not included in this calculation. |  |  |  |  | Step #7 | Calculate the total reserve required in the current year. Add the reserve required per year for each item to calculate the total reserve required in the current year. This is the estimated amount of money that your system needs to set aside, starting this current year, if you want to pay for all of these rehabilitation and replacement activities.
EXAMPLE Required Reserve Worksheet1
Date Worksheet Completed/Updated: 8/15/02
Asset (list from highest to lowest priority) | Activity | Years until action needed | Cost ($) | Reserve required current year
1. Chlorinator | Replace | 2 | 2000 | 1000
| Purchase redundant unit | 1 | 2000 | 2000
2. Pumphouse - Electrical | Replace with controller | 1 | 2000 | 2000
3. Well Pumps | Replace Well 1 pump | 1 | 5000 | 5000
| Replace Well 2 pump | 1 | 5000 | 5000
| Next Replacements (2 well pumps at $5000 each) | 10 | 10000 | 1000
4. Valves | Replacement | 31 | 22500 | 726
(45 valves at $500 each)
5. Hydrants | Replacement | 31 | 60000 | 1935
(30 hydrants at $2,000 each)
6. Pipe | 6-inch (3600 ft. at $20/ft.) | 51 | 302000 | 5922
4-inch (9500 ft. at $20/ft. - replace 4-inch with 6 inch)
2-inch (2000 ft. at $20/ft. - replace 2-inch with 6 inch)
(Total is 15,100 ft. at $20/ft.)
7. Storage | Rehabilitate 3 tanks | 5 | 50000 | 10000
(1 every 8 years, 1993 and 2000 tanks)
| Replace - 2 tanks (1993 tanks) | 31 | 40000 | 1290
| 1 tank (2000 tank) | 38 | 20000 | 526
Total reserve in the current year |  |  |  | 36399
1 Note: The Required Reserve Worksheet only helps you account for the additional funds you will require to rehabilitate or replace your asset. Standard O&M costs are not included in this calculation.

## Budgeting
Budgeting Worksheet |  |  | Instructions
Date worksheet completed/updated: 1 |  |  | Step #1 | Enter the date. Circle whether you are completing or updating the worksheet and fill in the date. You should update this worksheet once a year. You can either make minor adjustments to the worksheet, or start a new worksheet each year.
Revenues 2 | Expenses 4 | Net Income 6
Service Fees: | Maintenance: | Total Revenues:
| Utilities (power, telephone): | Total Expenses: | Step #2 | List your revenues. Fill in your revenues in the lines provided. If your system has other sources of income not listed on the worksheet, enter them in the “Other” lines provided.
Fees and Service Changes (late fee, connection fee, fire fee, etc.): | Salaries and Benefits:
| Equipment Cost: | Net Income (Revenue - Expenses): | Step #3 | Calculate total annual revenues. Calculate your total revenues by adding all the revenues you listed in the previous step. Enter this number in the box marked “Total Revenues.” Do not include funding you expect but have not secured.
Impact Fees (demand fee, system development fee, etc. ): | Chemicals:
Secured Funding: | Monitoring and Testing: |  | Step #4 | List your expenses. Fill in your expenses in the lines provided. If your system has other expenses not listed on the worksheet, enter them in the “Other” lines provided.
Interest: | Rent or Mortgage:
Other: | Insurance:
Additional Reserves Needed
| Professional Services (legal, accounting, engineering, etc.): | 7 Total Required Reserve: | Step #5 | Calculate total expenses. Calculate your total expenses by adding all the expenses you listed in the previous step. Enter this number in the box marked “Total Expenses.
Training Costs:
| Billing Costs: | 8 Net Income: | Step #6 | Calculate net income. Enter the result of step 3 on the “Total Revenues” line and the result of step 5 on the “Total Expenses” line. Calculate your net income by subtracting your expenses from your revenues. Enter this number on the “Net Income” line.
| Fees (state PWS fee, franchise fee, conservation fee, etc.): | 9 Additional Reserves Needed (Income - Required Reserves):
| Security: |  | Step #7 | Enter your total required reserves. Enter your total required reserves from the Required Reserves Worksheet.
Other (debt payments, taxes, miscellaneous, etc.):
|  |  | Step #8 | Enter your net income. Enter the result of step 6 on the “Net Income” line.
|  |  | Step #9 | Calculate additional reserves needed. Subtract your total required reserves (from step 7) from your net income (from step 8). Enter this number in the box marked “Additional Reserves Needed.” If the result is a positive number (i.e., your resources are larger than your required reserves), you will not have to plan for ways to make up for the shortfall and can set aside the required funds in a reserve account. If the result is a negative number (i.e., your resources are less than the required reserves), you should start planning for ways to make up for the shortfall.
Total Revenues: 3 | Total Expenses: 5